## Slide 1
Precision Timing for Digital Substations
Fred Steinhauser, Digital Substation Evangelist

## Slide 2: Who I am
University of Technology Vienna
1981-1990
Master, Ph.D., Research Assistant
Process Automation & IT in textile industry
1990-1998
OMICRON
1998-2014 | Product Management
2001-... | Involvement into IEC 61850
2014-... | Fully dedicated to Power Utility Communication
2018-... | Digital Substation Evangelist

## Slide 3: and Precision Timing?
Test equipment for testing power system assets
Protection Testing End-to-End testing
Distributed, time synchronized testing (since about 1993)
Power Utility Communication – IEC 61850
Assessment of communication networks for Digital Substations Propagation delays, ...
Distributed, time synchronized testing
Tools made for electrical power engineers
Different usability than for, e.g., telecom engineers

## Slide 4: Applications Depending on Precision Timing
Much fostered by the advent of GNSS
Differential protection
Fault location
Synchrophasors
End-to-End testing
Fault analysis

## Slide 5
Fault Analysis
2003 Blackout

## Slide 6
Proposed measures
2003 Blackout

## Slide 7: Applications on the Uncertainty Scale
Well covered with PTP (and related profiles)
1 ms
Fault
location
Synchrophasors
Control SCADA logs
Sequence of events
1 s
1 ns
1 µs
Sampled
Values
Self-synchronizing Differential protection

## Slide 8: Application Uncertainty Reference
Power system frequencies – 50 Hz / 60 Hz
Time Error | Phase Error @ 50 Hz | Phase Error @ 60 Hz
1 ms | 18° | 21.6°
100 µs | 1.8° | 2.2°
55.5 µs | 1.0° | 1.2°
46,3 µs | 0.8° | 1.0°
Ballpark figures
50 µs ≈ 1°
5 µs ≈ 0.1°
1 µs ≈ 1.2 minutes
(360° corresponds to one cycle of the power system)

## Slide 9: Sampled Values: Sampling Timing in "9-2LE"
1µs

## Slide 10: Requirements for PMUs
Total Vector Error
(Total Phasor Error)
Combination of errors
Magnitude error Phase- (time-) error
PMUs work well ...
... with time uncertainties of about 10 µs

## Slide 11: PTP Profiles
IEC 61850-9-3
Power Utility Profile
Close to the Standard Profile Basic profile
IEEE C37.238
Power Profile
Common properties
Layer 2
Peer-to-peer

## Slide 12: Accuracy along the time distribution chain
Maximum time synchronization uncertainty
1 µs over 16 hops
1 hop
± 50 ns
± 200 ns
IED to be
synchronized
max. 16 hops
max. 16 ∙± 50 ns = ± 800 ns

## Slide 13: Accuracy along the time distribution chain
-550 ns
+550 ns
Assume uniform distribution at the "contributors" Uniform distribution = conservative assumption Master clock
Transparent clock
Do the math ...
... for the entire chain with 16 hops
Matches simulation
2 ∙ 𝜎CH

## Slide 14: The Power Utility Mindset

## Slide 15: Field of Expertise with Tradition
More than 100 years ...

## Slide 16: Power Systems started without Precision Timing
Much was achieved without precision timing
Established methods are seen as the reference
Paul Watzlawick – Psychologist, Author: Anleitung zum Unglücklichsein (Guide to Unhappiness) Wenn die Loesung das Problem ist (1987) (When the solution is the problem) https://www.youtube.com/watch?v=cl4aZTPsTSs
Precision timing-based methods are seen as "nice to have" extensions
Reliance on precision timing is not desired
The power industry has not yet fully embraced precision timing

## Slide 17: Lack of Embracement
Poll at webinar in March 2022
"Enabling wide area protection with IEC 61850"
Expected audience (at least for me)
Open minds
Familiar with time sync topic
Tech affine
Only 48% ...
... regarded precision time sync as a future need

## Slide 18: Power Utility Value Perception
HV Circuit Breaker HV Protection Relay
Ethernet Switch
GNSS/PTP
Master Clock
≈ 100 k€ | ≈ 10 k€ | ≈ 10 k€ | ≈ 5 k€
accepted  | accepted  | expensive ! | expensive !

## Slide 19: Apprehensions
Emphasizing on threats
What if ...?
But there may be GNSS jamming!
But there may be GNSS spoofing!
...

## Slide 20: Components vs. Solutions

## Slide 21: What makes a Precision Timing Solution?
Components are readily available
GNSS receivers
Master clocks, boundary clocks
PTP and its parameters
PTP transparent Ethernet switches
Oscillators with long holdover time (atomic clocks)
....

## Slide 22: Precision Timing System Integration
Putting the components together
Set of complex tasks
Designing the precision timing system Building the system
Configuring the system
Testing the system
Who can do that?

## Slide 23: What I wish to see
GNSS 1 (e.g., GPS)
GNSS 2
(e.g., Galileo)
Time assessor & dispatcher
Precision time for the
Digital Substation
Atomic clock
"Super Master Clock"
"All bases covered" solution
Perceived problems addressed
Solutions explained
Holdover specified
Implementation described
Offer for the integrated solution

## Slide 24: Redundant Time Synchronization
Reliable clock failover scenarios
Straps and belts can make things complicated
Best practice still evolving
Guidance welcome
To be thoroughly tested

## Slide 25: Timescale
Sentral Clocknode
Sentral Clocknode
GNSS
GNSS
ePRTC (cnPRTC)
Cesium
Offset generator
Distribution amplifier / Phase comp
Cesium
Offset generator Distribution amplifier
White Rabbitlink
Source: Presentation from Statnett (Norway) at
ITSF 2022

## Slide 26: Time Appliance in the Electrical Power Industry

## Slide 27: Substation Devices
Dedicated hardware
No habitat for a standard PCI card

## Slide 28: Trend: Application Servers
Virtualized devices
Possible habitat for a standard PCI card

## Slide 29: "Holdover is our best friend!"
Heiko Gerstung
ITSF 2022
Continuous delivery of time
No hiccups in dependent functions
due to intermittent time synchronization
Atomic clocks in servers "Chip Scale Atomic Clock "Micro Atomic Clock"
...

## Slide 30: Open Source in the Electrical Power Industry

## Slide 31: Open Source in the Electrical Power Industry
Linux Foundation - LF Energy
https://www.lfenergy.org/projects/
RTE - commitment to Open Source

## Slide 32: Open Source in the Electrical Power Industry
https://www.alliander.com/en/open-source/projects/
https://www.lfenergy.org/projects/compas/
Open Source virtualization platform for centralized protection ?
IEC 61850 Engineering – OpenSCD

## Slide 33: Manipulate IEC 61850 System Configuration (SCL)
https://OpenSCD.github.io

## Slide 34: Summary

## Slide 35: Let's summarize ...
Applications in power systems that benefit from or even require precision timing do exist
The value of precisely time synchronized systems is not yet fully recognized
Possible solutions exist but are not well known - must be better communicated and promoted
Application servers may be a habitat for the Time Card
Open Source projects are in progress

## Slide 36: Thank you ...
fred.steinhauser@omicronenergy.com
www.linkedin.com/in/fredsteinhauser
... for your attention